SEWER SPECIFICAITONS

FOR

WILL ROGERS DOWN KOA SEWER EXTENSION

OCTOBER 2024

SECTION 33 52 00 – FACILITY SANITARY SEWERS

PART 1 - GENERAL

* 1. RELATED DOCUMENTS
     1. Lift Station Specifications
  2. SUMMARY
     1. Section Includes:
        1. PVC pipe and fittings.
        2. Nonpressure-type transition couplings.
        3. Pressure-type pipe couplings.
        4. Expansion joints and deflection fittings.
        5. Backwater valves.
        6. Cleanouts.
        7. Encasement for piping.
        8. Manholes.
        9. Concrete.
  3. DEFINITIONS
     1. The following are industry abbreviations for materials:

EPDM: Ethylene-propylene-diene-monomer rubber. PVC: Polyvinyl chloride plastic.

TPE: Thermoplastic elastomer.

* 1. ACTION SUBMITTALS
     1. Product Data: For the following:
        1. Pipe and fittings.
        2. Non-pressure and pressure couplings
        3. Expansion joints and deflection fittings.
        4. Backwater valves.
        5. Cleanouts.
     2. Shop Drawings: For manholes. Include plans, elevations, sections, details, and frames and covers.
  2. INFORMATIONAL SUBMITTALS
     1. Coordination Drawings:
        1. Show pipe sizes, locations, and elevations. Show other piping in same trench and clearances from sewer system piping. Indicate interface and spatial relationship between manholes, piping, and proximate structures.
     2. Product Certificates: For each type of pipe and fitting.
     3. Field quality-control reports.
  3. DELIVERY, STORAGE, AND HANDLING
     1. Do not store plastic pipe, and fittings in direct sunlight.
     2. Protect pipe, pipe fittings, and seals from dirt and damage.
     3. Handle manholes according to manufacturer's written rigging instructions.
  4. FIELD CONDITIONS
     1. Interruption of Existing Sanitary Sewerage Service: Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:
        1. Notify Owner no fewer than two days in advance of proposed interruption of service.
        2. Do not proceed with interruption of service without Owner's written permission.

PART 2 - PRODUCTS

* 1. PVC PIPE AND FITTINGS
     1. PVC, Schedule 40 and 80 Pipe: ASTM D 1785.
        1. PVC, Schedule 40 and 80 Socket Fittings: ASTM D 2466.
     2. PVC Type PSM Sewer Piping:
        1. Pipe: ASTM D 3034, [SDR 35] [SDR 26], PVC Type PSM sewer pipe with bell-and- spigot ends for gasketed joints, for diameters of 8 inches to 15 inches
        2. Fittings: ASTM D 3034, PVC with bell ends.
        3. Gaskets: ASTM F 477, elastomeric seals.
  2. NONPRESSURE-TYPE TRANSITION COUPLINGS
     1. Comply with ASTM C 1173, elastomeric, sleeve-type, reducing or transition coupling; for joining underground nonpressure piping. Include ends of same sizes as piping to be joined and include corrosion-resistant-metal tension band and tightening mechanism on each end.
     2. Sleeve Materials:
        1. For Plastic Pipes: ASTM F 477, elastomeric seal or ASTM D 5926, PVC.
        2. For Dissimilar Pipes: ASTM D 5926, PVC or other material compatible with pipe materials being joined.
     3. Nonpressure-Type, Rigid Couplings:
        1. Description: ASTM C 1461, sleeve-type, reducing- or transition-type mechanical coupling; molded from ASTM C 1440, TPE material; with corrosion-resistant-metal tension band and tightening mechanism on each end.
  3. PRESSURE-TYPE PIPE COUPLINGS
     1. Tubular-Sleeve Couplings: AWWA C219, with center sleeve, gaskets, end rings, and bolt fasteners.
     2. Metal, bolted, sleeve-type, reducing or transition coupling; for joining underground pressure piping. Include 200-psig minimum pressure rating and ends of same sizes as piping to be joined.
     3. Center-Sleeve Material: Manufacturer's standard.
     4. Gasket Material: Natural or synthetic rubber.
     5. Metal Component Finish: Corrosion-resistant coating or material.
  4. EXPANSION JOINTS AND DEFLECTION FITTINGS
     1. Ductile-Iron Expansion Joints:
        1. Description: Three-piece assembly of telescoping sleeve with gaskets and restrained-type, ductile-iron, bell-and-spigot end sections complying with AWWA C110/A21.10 or AWWA C153/A21.53. Include rating for 250-psig minimum working pressure and for expansion indicated.
     2. Ductile-Iron Deflection Fittings:
        1. Description: Compound coupling fitting with ball joint, flexing section, gaskets, and restrained-joint ends complying with AWWA C110/A21.10 or AWWA C153/A21.53.

Include rating for 250-psig minimum working pressure and for up to 15 degrees of deflection.

* 1. BACKWATER VALVES
     1. Cast-Iron Backwater Valves:
        1. Description: ASME A112.14.1, gray-iron body and bolted cover, with bronze seat.
        2. Horizontal type; with swing check valve and hub-and-spigot ends.
        3. Combination horizontal and manual gate-valve type; with swing check valve, integral gate valve, and hub-and-spigot ends.
        4. Terminal type; with bronze seat, swing check valve, and hub inlet.
  2. CLEANOUTS
     1. Cast-Iron Cleanouts:
        1. Description: ASME A112.36.2M, round, gray-iron housing with clamping device and round, secured, scoriated, gray-iron cover. Include gray-iron ferrule with inside calk or spigot connection and countersunk, tapered-thread, brass closure plug.
        2. Top-Loading Classification(s): as indicated on plans and according to section 3.7 below
        3. Sewer Pipe Fitting and Riser to Cleanout: ASTM A 74, Service class, cast-iron soil pipe and fittings.
     2. PVC Cleanouts:
        1. Description: PVC body with PVC threaded plug. Include PVC sewer pipe fitting and riser to cleanout of same material as sewer piping.

|  |  |  |
| --- | --- | --- |
| 2.7 |  | ENCASEMENT FOR PIPING |
|  | A. | Standard: ASTM A 674 or AWWA C105/A21.5. |
|  | B. | Material: Linear low-density polyethylene film of 0.008-inch minimum thickness. |
|  | C. | Form: tube. |
|  | D. | Color: Black |
| 2.8 |  | MANHOLES |
|  | A. | Standard Precast Concrete Manholes: |
|  |  | 1. Description: ASTM C 478, precast, reinforced concrete, of depth indicated, with provision for sealant joints. |

* + - 1. Diameter: 48 inches minimum unless otherwise indicated.
      2. Ballast: Increase thickness of precast concrete sections or add concrete to base section, as required to prevent flotation.
      3. Base Section: 6-inch minimum thickness for floor slab and 4-inch minimum thickness for walls and base riser section; with separate base slab or base section with integral floor.
      4. Riser Sections: 4-inch minimum thickness, of length to provide depth indicated.
      5. Top Section: Eccentric-cone type unless concentric-cone or flat-slab-top type is indicated; with top of cone of size that matches grade rings.
      6. Joint Sealant: ASTM C 990, bitumen or butyl rubber.
      7. Resilient Pipe Connectors: ASTM C 923, cast or fitted into manhole walls, for each pipe connection.
      8. Steps: ASTM A 615**,** deformed, 1/2-inch steel reinforcing rods encased in ASTM D 4101, PP; wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step. Cast or anchor steps into sidewalls at 12- to 16-inch intervals. Omit steps if total depth from floor of manhole to finished grade is less than 60 inches**.**
      9. Grade Rings: Reinforced-concrete rings, 6- to 9-inch total thickness, with diameter matching manhole frame and cover, and with height as required to adjust manhole frame and cover to indicated elevation and slope.

1. Designed Precast Concrete Manholes:
   1. Description: ASTM C 913; designed according to ASTM C 890 for A-16 (ASSHTO HS20-44 in AASHTO HL), heavy-traffic, structural loading; of depth, shape, and dimensions indicated, with provision for sealant joints.
   2. Ballast: Increase thickness of one or more precast concrete sections or add concrete to manhole as required to prevent flotation.
   3. Joint Sealant: ASTM C 990, bitumen or butyl rubber.
   4. Resilient Pipe Connectors: ASTM C 923, cast or fitted into manhole walls, for each pipe connection.
   5. Steps: ASTM A 615/A 615M, deformed, 1/2-inch steel reinforcing rods encased in ASTM D 4101, PP; wide enough to allow worker to place both feet on one step and designed to prevent lateral slippage off step. Cast or anchor steps into sidewalls at 12- to 16-inch intervals. Omit steps if total depth from floor of manhole to finished grade is less than 60 inches**.**
   6. Grade Rings: Reinforced-concrete rings, 6- to 9-inch total thickness, with diameter matching manhole frame and cover, and with height as required to adjust manhole frame and cover to indicated elevation and slope.
2. Manhole Frames and Covers:
   1. Description: Ferrous; 24-inch ID by 7- to 9-inch riser, with 4-inch- minimum-width flange and 26-inch- diameter cover. Include indented top design with lettering cast into cover, using wording equivalent to "SANITARY SEWER."
   2. Material: ASTM A 48/A 48M, Class 35 gray iron unless otherwise indicated.
3. Manhole-Cover Inserts:
   1. Description; Manufactured, plastic form, of size to fit between manhole frame and cover and designed to prevent stormwater inflow. Include handle for removal and gasket for gastight sealing.
   2. Type: Solid
   3. CONCRETE
      1. General: Cast-in-place concrete complying with ACI 318, ACI 350, and the following:
         1. Cement: ASTM C 150, Type II.
         2. Fine Aggregate: ASTM C 33, sand.
         3. Coarse Aggregate: ASTM C 33, crushed gravel.
         4. Water: Potable.
      2. Portland Cement Design Mix: 4000 psi minimum, with 0.45 maximum water/cementitious materials ratio.
         1. Reinforcing Bars: ASTM A 615, Grade 60 deformed steel.
      3. Manhole Channels and Benches: Factory or field formed from concrete. Portland cement design mix, 4000 psi minimum, with 0.45 maximum water/cementitious materials ratio. Include channels and benches in manholes.
         1. Channels: Concrete invert, formed to same width as connected piping, with height of vertical sides to three-fourths of pipe diameter. Form curved channels with smooth, uniform radius and slope.
            1. Invert Slope: 2 percent through manhole.
         2. Benches: Concrete, sloped to drain into channel.
            1. Slope: 8 percent.
      4. Ballast and Pipe Supports: Portland cement design mix, 3000 psi minimum, with 0.58 maximum water/cementitious materials ratio.
         1. Reinforcing Bars: ASTM A 615/A 615M, Grade 60 deformed steel.

PART 3 - EXECUTION

* 1. EARTHWORK
     1. Excavating, trenching, and backfilling are specified in Section 31 20 00 "Earth Moving."
  2. PIPING INSTALLATION
     1. General Locations and Arrangements: Drawing plans and details to indicate general location and arrangement of underground sanitary sewer piping. Location and arrangement of piping layout take into account design considerations. Install piping as indicated, to extent practical. Where specific installation is not indicated, follow piping manufacturer's written instructions.
     2. Install piping beginning at low point, true to grades and alignment indicated with unbroken continuity of invert. Place bell ends of piping facing upstream. Install gaskets, seals, sleeves, and couplings according to manufacturer's written instructions for using lubricants, cements, and other installation requirements.
     3. Install manholes for changes in direction unless fittings are indicated. Use fittings for branch connections unless direct tap into existing sewer is indicated.
     4. Install proper size increasers, reducers, and couplings where different sizes or materials of pipes and fittings are connected. Reducing size of piping in direction of flow is prohibited.
     5. When installing pipe under streets or other obstructions that cannot be disturbed, use pipe- jacking process of microtunneling, boring or combination of any.
     6. Install gravity-flow, nonpressure, drainage piping according to the following:
        1. Install piping pitched down in direction of flow, at minimum slope of 1 percent unless otherwise indicated.
        2. Install piping NPS 6 and larger with restrained joints at tee fittings and at changes in direction. Use corrosion-resistant rods, pipe or fitting manufacturer's proprietary restraint system, or cast-in-place-concrete supports or anchors.
        3. Install piping with 30-inch minimum cover.
        4. Install piping below frost line.
        5. Install ductile-iron, gravity sewer piping according to ASTM A 746.
        6. Install PVC profile sewer piping according to ASTM D 2321 and ASTM F 1668.
        7. Install PVC Type PSM sewer piping according to ASTM D 2321 and ASTM F 1668.
     7. Install force-main, pressure piping according to the following:
        1. Install piping with restrained joints at tee fittings and at horizontal and vertical changes in direction. Use corrosion-resistant rods, pipe or fitting manufacturer's proprietary restraint system, or cast-in-place-concrete supports or anchors.
        2. Install piping with 36-inch minimum cover.
        3. Install piping below frost line.
        4. Install ductile-iron pressure piping according to AWWA C600 or AWWA M41.
        5. Install ductile-iron special fittings according to AWWA C600.
        6. Install PVC pressure piping according to AWWA M23 or to ASTM D 2774 and ASTM F 1668.
        7. Install PVC water-service piping according to ASTM D 2774 and ASTM F 1668.
     8. Install corrosion-protection piping encasement over the following underground metal piping according to ASTM A 674 or AWWA C105/A21.5:
        1. Ductile-iron pipe and fittings.
        2. Expansion joints and deflection fittings.
     9. Clear interior of piping and manholes of dirt and superfluous material as work progresses. Maintain swab or drag in piping, and pull past each joint as it is completed. Place plug in end of incomplete piping at end of day and when work stops.
  3. PIPE JOINT CONSTRUCTION
     1. Join gravity-flow, nonpressure, drainage piping according to the following:
        1. Join ductile-iron, gravity sewer piping according to AWWA C600 for push-on joints.
        2. Join PVC profile sewer piping according to ASTM D 2321 for elastomeric-seal joints or ASTM F 794 for gasketed joints.
        3. Join PVC Type PSM sewer piping according to ASTM D 2321 and ASTM D 3034 for elastomeric-seal joints or ASTM D 3034 for elastomeric-gasket joints.
        4. Join PVC gravity sewer piping according to ASTM D 2321 and ASTM D 3034 for elastomeric-seal joints or ASTM D 3034 for elastomeric-gasket joints.
        5. Join dissimilar pipe materials with nonpressure-type, rigid couplings.
     2. Join force-main, pressure piping according to the following:
        1. Join ductile-iron pressure piping according to AWWA C600 or AWWA M41 for push-on joints.
        2. Join ductile-iron special fittings according to AWWA C600 or AWWA M41 for push-on joints.
        3. Join PVC pressure piping according to AWWA M23 for gasketed joints.
        4. Join dissimilar pipe materials with pressure-type couplings.
     3. Pipe couplings, expansion joints, and deflection fittings with pressure ratings at least equal to piping rating may be used in applications below unless otherwise indicated.
        1. Use pressure pipe couplings for force-main joints.
  4. MANHOLE INSTALLATION
     1. General: Install manholes complete with appurtenances and accessories indicated.
     2. Install precast concrete manhole sections with sealants according to ASTM C 891.
     3. Install FRP manholes according to manufacturer's written instructions.
     4. Form continuous concrete channels and benches between inlets and outlet.
     5. Set tops of frames and covers flush with finished surface of manholes that occur in pavements. Set tops 3 inches above finished surface elsewhere unless otherwise indicated.
     6. Install manhole-cover inserts in frame and immediately below cover.
  5. CONCRETE PLACEMENT
     1. Place cast-in-place concrete according to ACI 318.
  6. BACKWATER VALVE INSTALLATION
     1. Install horizontal-type backwater valves in piping manholes or pits.
     2. Install combination horizontal and manual gate-type valves in piping and in manholes.
     3. Install terminal-type backwater valves on end of piping and in manholes. Secure units to sidewalls.
  7. CLEANOUT INSTALLATION
     1. Install cleanouts and riser extensions from sewer pipes to cleanouts at grade. Use cast-iron soil pipe fittings in sewer pipes at branches for cleanouts, and use cast-iron soil pipe for riser extensions to cleanouts. Install piping so cleanouts open in direction of flow in sewer pipe.
        1. Use Light-Duty, top-loading classification cleanouts in earth or unpaved foot-traffic areas.
        2. Use Medium-Duty, top-loading classification cleanouts in paved foot-traffic areas.
        3. Use Heavy-Duty, top-loading classification cleanouts in vehicle-traffic service areas.
        4. Use Extra-Heavy-Duty, top-loading classification cleanouts in roads .
     2. Set cleanout frames and covers in earth in cast-in-place-concrete block, 12 by 12 by 6 inches deep. Set with tops 1 inch above surrounding grade.
     3. Set cleanout frames and covers in concrete pavement and roads with tops flush with pavement surface.
  8. CONNECTIONS
     1. Make connections to existing piping and underground manholes.
        1. Use commercially manufactured wye fittings for piping branch connections. Remove section of existing pipe, install wye fitting into existing piping, and encase entire wye fitting plus 6-inch overlap with not less than 6 inches of concrete with 28-day compressive strength of 3000 psi.
        2. Make branch connections from side into existing piping, NPS 4 to NPS 20. Remove section of existing pipe, install wye fitting into existing piping, and encase entire wye with not less than 6 inches of concrete with 28-day compressive strength of 3000 psi.
        3. Make branch connections from side into existing piping, NPS 21 or larger, or to underground manholes by cutting opening into existing unit large enough to allow 3 inches of concrete to be packed around entering connection. Cut end of connection pipe passing through pipe or structure wall to conform to shape of, and be flush with, inside wall unless otherwise indicated. On outside of pipe or manhole wall, encase entering connection in 6 inches of concrete for minimum length of 12 inches to provide additional support of collar from connection to undisturbed ground.
           1. Use concrete that will attain a minimum 28-day compressive strength of 3000 psi unless otherwise indicated.
           2. Use epoxy-bonding compound as interface between new and existing concrete and piping materials.
        4. Protect existing piping and manholes to prevent concrete or debris from entering while making tap connections. Remove debris or other extraneous material that may accumulate.
  9. CLOSING ABANDONED SANITARY SEWER SYSTEMS
     1. Abandoned Piping: Close open ends of abandoned underground piping indicated to remain in place. Include closures strong enough to withstand hydrostatic and earth pressures that may result after ends of abandoned piping have been closed. Use either procedure below:
        1. Close open ends of piping with at least 8-inch- thick, bulkheads made from flowable fill.
        2. Close open ends of piping with threaded metal caps, plastic plugs, or other acceptable methods suitable for size and type of material being closed. Do not use wood plugs.
     2. Abandoned Manholes: Excavate around manhole as required and use either procedure below:
        1. Remove manhole and close open ends of remaining piping.
        2. Remove top of manhole down to at least 36 inches below final grade. Close open ends of piping. Fill to within 12 inches of top with stone, rubble, gravel, or compacted dirt. Fill to top with concrete.
     3. Backfill to grade according to Construction Details.
  10. FIELD QUALITY CONTROL
      1. Inspect interior of piping to determine whether line displacement or other damage has occurred. Inspect after approximately 24 inches of backfill is in place, and again at completion of Project.
         1. Submit separate report for each system inspection.
         2. Defects requiring correction include the following:
            1. Alignment: Less than full diameter of inside of pipe is visible between structures.
            2. Deflection: Flexible piping with deflection that prevents passage of ball or cylinder of size not less than 92.5 percent of piping diameter.
            3. Damage: Crushed, broken, cracked, or otherwise damaged piping.
            4. Infiltration: Water leakage into piping.
            5. Exfiltration: Water leakage from or around piping.
         3. Replace defective piping using new materials, and repeat inspections until defects are within allowances specified.
         4. Reinspect and repeat procedure until results are satisfactory.
      2. Test new piping systems, and parts of existing systems that have been altered, extended, or repaired, for leaks and defects.
         1. Do not enclose, cover, or put into service before inspection and approval.
         2. Test completed piping systems according to requirements of authorities having jurisdiction.
         3. Schedule tests and inspections by authorities having jurisdiction with at least 24 hours' advance notice.
         4. Submit separate report for each test.
         5. Hydrostatic Tests: Test sanitary sewerage according to requirements of authorities having jurisdiction and the following:
            1. Fill sewer piping with water. Test with pressure of at least 10-foot head of water, and maintain such pressure without leakage for at least 15 minutes.
            2. Allowable leakage is maximum of 50 gal./inch of nominal pipe size per mile of pipe, during 24-hour period.
            3. Close openings in system and fill with water.
            4. Purge air and refill with water.
            5. Disconnect water supply.
            6. Test and inspect joints for leaks.
         6. Air Tests: Test sanitary sewerage according to requirements of authorities having jurisdiction, UNI-B-6, and the following:
            1. Test plastic gravity sewer piping according to ASTM F 1417.
         7. Force Main: Perform hydrostatic test after thrust blocks, supports, and anchors have hardened. Test at pressure not less than 1-1/2 times the maximum system operating pressure, but not less than 150 psig.
            1. Ductile-Iron Piping: Test according to AWWA C600
            2. PVC Piping: Test according to AWWA M23
         8. Manholes: Perform hydraulic test according to ASTM C 969.
      3. Leaks and loss in test pressure constitute defects that must be repaired.
      4. Replace leaking piping using new materials, and repeat testing until leakage is within allowances specified.
  11. CLEANING
      1. Clean dirt and superfluous material from interior of piping. Flush with potable water.

END OF SECTION33 52 00